## README
The Excel file describes the parameters of all components in the 240-node distribution test system. The components include the equivalent source, substation transformer, lines (including line configuration), secondary distribution transformer, circuit breaker, shunt capacitor bank, and load.

## Equivalent Source
Equivalent Voltage Source
Nominal Voltage | p.u. | Voltage angle (°) | Positive-sequence resistance (Ω) | Positive-sequence reactance (Ω) | Zero-sequence resistance (Ω) | Zero-sequence reactance (Ω)
69 kV | 1 | 0 | 4.5426 | 10.5274 | 7.3655 | 24.5046

## Substation Transformer
Subtation Transformer
Name | Bus A | Bus B | kVA rating (kVA) | Primary voltage rating (kV) & Connection | Secondary voltage rating (kV) & Connection | R - % | X - %
Sub_Xfmr | eq_source_bus | bus_Xfmr | 10000 | 69 - Delta | 13.8 Gr-Wye | 0.62659 | 6.2659
Tap Changer
Name | sub_regulator_A | sub_regulator_B | sub_regulator_C
kVA rating (kVA) | 3500 | 3500 | 3500
Phase | A | B | C
Bus A | bus_Xfmr | bus_Xfmr | bus_Xfmr
Bus B | bus1 | bus1 | bus1
Connection | Grd.-Wye | Grd.-Wye | Grd.-Wye
Monitoring bus | Bus 1, Phase A | Bus 1, Phase B | Bus 1, Phase C
Primary voltage rating (kV) | 7.9677 | 7.9677 | 7.9677
Secondary voltage rating (kV) | 7.9677 | 7.9677 | 7.9677
PT ratio | 66.3953 | 66.3953 | 66.3953
Voltge setting (V) | 123 | 123 | 123
Voltage bandwidth (V) | 2 | 2 | 2
Maximum voltage limit (V) | 129 | 129 | 129
Number of taps | 32 | 32 | 32

## Line Data
Line Segment Data (Feeder A) | [5 empty] | Line Segment Data (Feeder B) | [5 empty] | Line Segment Data (Feeder C)
Name | Bus A | Bus B | Length(ft.) | Phases | Config. | Name | Bus A | Bus B | Length(ft.) | Phase | Config. | Name | Bus A | Bus B | Length(ft.) | Phase | Config.
L_1001_1002 | 1001 | 1002 | 2967 | ABC | UG_3p_type1 | L_2001_2002 | 2001 | 2002 | 1388 | ABC | UG_3p_type1 | L_3001_3003 | 3001 | 3003 | 2307 | ABC | UG_3p_type1
L_1002_1003 | 1002 | 1003 | 372 | ABC | UG_3p_type2 | L_2002_2003 | 2002 | 2003 | 1281 | ABC | OH_3p_type1 | L_3003_3002 | 3003 | 3002 | 85 | ABC | UG_3p_type2
L_1002_1004 | 1002 | 1004 | 638 | ABC | OH_3p_type1 | L_2003_2004 | 2003 | 2004 | 798 | ABC | OH_3p_type1 | L_3003_3004 | 3003 | 3004 | 81 | ABC | UG_3p_type2
L_1004_1005 | 1004 | 1005 | 394 | ABC | OH_3p_type1 | L_2004_2005 | 2004 | 2005 | 317 | ABC | OH_3p_type1 | L_3003_3005 | 3003 | 3005 | 1997 | ABC | UG_3p_type1
L_1005_1006 | 1005 | 1006 | 1049 | ABC | OH_3p_type1 | L_2005_2006 | 2005 | 2006 | 145 | ABC | OH_3p_type1 | L_3005_3006 | 3005 | 3006 | 311 | ABC | OH_3p_type1
L_1006_1007 | 1006 | 1007 | 2000 | AB | OH_2p_type2 | L_2006_2007 | 2006 | 2007 | 245 | A | OH_1p_type5 | L_3006_3007 | 3006 | 3007 | 370 | ABC | OH_3p_type1
L_1006_1008 | 1006 | 1008 | 454 | ABC | OH_3p_type1 | L_2007_2008 | 2007 | 2008 | 125 | A | UG_1p_type2 | L_3005_3008 | 3005 | 3008 | 136 | ABC | OH_3p_type1
L_1008_1009 | 1008 | 1009 | 1082 | ABC | OH_3p_type1 | L_2007_2009 | 2007 | 2009 | 161 | A | OH_1p_type2 | L_3008_3009 | 3008 | 3009 | 161 | A | OH_1p_type5
L_1009_1010 | 1009 | 1010 | 169 | ABC | OH_3p_type1 | L_2006_2010 | 2006 | 2010 | 170 | ABC | OH_3p_type1 | L_3009_3010 | 3009 | 3010 | 347 | A | OH_1p_type5
L_1009_1011 | 1009 | 1011 | 60 | ABC | UG_3p_type2 | L_2010_2011 | 2010 | 2011 | 275 | ABC | OH_3p_type1 | L_3010_3011 | 3010 | 3011 | 265 | A | OH_1p_type5
L_1011_1012 | 1011 | 1012 | 60 | ABC | UG_3p_type2 | L_2011_2012 | 2011 | 2012 | 503 | ABC | OH_3p_type1 | L_3011_3012 | 3011 | 3012 | 312 | A | OH_1p_type5
L_1012_1013 | 1012 | 1013 | 306 | ABC | UG_3p_type2 | L_2013_2014 | 2013 | 2014 | 268 | ABC | OH_3p_type1 | L_3008_3013 | 3008 | 3013 | 170 | B | OH_1p_type5
L_1013_1014 | 1013 | 1014 | 208 | B | UG_1p_type2 | L_2014_2015 | 2014 | 2015 | 120 | B | UG_1p_type2 | L_3013_3014 | 3013 | 3014 | 295 | B | OH_1p_type5
L_1014_1015 | 1014 | 1015 | 126 | B | UG_1p_type2 | L_2014_2016 | 2014 | 2016 | 257 | ABC | OH_3p_type1 | L_3008_3015 | 3008 | 3015 | 322 | ABC | OH_3p_type1
L_1013_1016 | 1013 | 1016 | 468 | C | UG_1p_type2 | L_2016_2017 | 2016 | 2017 | 174 | ABC | UG_3p_type2 | L_3015_3016 | 3015 | 3016 | 210 | B | OH_1p_type5
L_1016_1017 | 1016 | 1017 | 71 | C | UG_1p_type2 | L_2017_2018 | 2017 | 2018 | 447 | ABC | UG_3p_type2 | L_3016_3017 | 3016 | 3017 | 259 | B | OH_1p_type5
[6 empty] | L_2013_2019 | 2013 | 2019 | 45 | ABC | OH_3p_type1 | L_3015_3018 | 3015 | 3018 | 181 | C | OH_1p_type5
[6 empty] | L_2019_2020 | 2019 | 2020 | 642 | B | UG_1p_type2 | L_3018_3019 | 3018 | 3019 | 281 | C | OH_1p_type5
[6 empty] | L_2019_2021 | 2019 | 2021 | 43 | ABC | OH_3p_type1 | L_3019_3020 | 3019 | 3020 | 307 | C | OH_1p_type5
[6 empty] | L_2021_2022 | 2021 | 2022 | 205 | C | UG_1p_type2 | L_3020_3021 | 3020 | 3021 | 303 | C | OH_1p_type5
[6 empty] | L_2022_2023 | 2022 | 2023 | 150 | C | UG_1p_type2 | L_3015_3022 | 3015 | 3022 | 289 | ABC | OH_3p_type1
[6 empty] | L_2023_2024 | 2023 | 2024 | 408 | C | UG_1p_type2 | L_3022_3023 | 3022 | 3023 | 181 | A | OH_1p_type5
[6 empty] | L_2024_2025 | 2024 | 2025 | 331 | C | UG_1p_type2 | L_3023_3024 | 3023 | 3024 | 320 | A | OH_1p_type5
[6 empty] | L_2026_2027 | 2026 | 2027 | 369 | ABC | OH_3p_type1 | L_3024_3025 | 3024 | 3025 | 331 | A | OH_1p_type5
[6 empty] | L_2027_2028 | 2027 | 2028 | 285 | ABC | UG_3p_type2 | L_3022_3026 | 3022 | 3026 | 164 | A | OH_1p_type5
[6 empty] | L_2028_2029 | 2028 | 2029 | 131 | ABC | UG_3p_type2 | L_3026_3027 | 3026 | 3027 | 368 | A | OH_1p_type5
[6 empty] | L_2029_2030 | 2029 | 2030 | 165 | ABC | UG_3p_type2 | L_3027_3028 | 3027 | 3028 | 241 | A | OH_1p_type5
[6 empty] | L_2030_2031 | 2030 | 2031 | 245 | ABC | UG_3p_type2 | L_3028_3029 | 3028 | 3029 | 317 | A | OH_1p_type5
[6 empty] | L_2027_2032 | 2027 | 2032 | 149 | ABC | OH_3p_type1 | L_3022_3030 | 3022 | 3030 | 304 | ABC | OH_3p_type1
[6 empty] | L_2032_2033 | 2032 | 2033 | 289 | ABC | OH_3p_type1 | L_3030_3035 | 3030 | 3035 | 103 | ABC | OH_3p_type1
[6 empty] | L_2033_2034 | 2033 | 2034 | 185 | ABC | OH_3p_type5 | L_3035_3036 | 3035 | 3036 | 271 | ABC | OH_3p_type1
[6 empty] | L_2033_2035 | 2033 | 2035 | 160 | ABC | OH_3p_type1 | L_3036_3037 | 3036 | 3037 | 136 | ABC | OH_3p_type1
[6 empty] | L_2035_2036 | 2035 | 2036 | 160 | ABC | OH_3p_type1 | L_3037_3038 | 3037 | 3038 | 252 | ABC | OH_3p_type1
[6 empty] | L_2036_2037 | 2036 | 2037 | 80 | ABC | OH_3p_type1 | L_3038_3039 | 3038 | 3039 | 235 | ABC | OH_3p_type1
[6 empty] | L_2037_2038 | 2037 | 2038 | 192 | ABC | OH_3p_type1 | L_3039_3053 | 3039 | 3053 | 263 | ABC | OH_3p_type1
[6 empty] | L_2038_2039 | 2038 | 2039 | 800 | ABC | OH_3p_type1 | L_3053_3054 | 3053 | 3054 | 280 | ABC | UG_3p_type2
[6 empty] | L_2039_2040 | 2039 | 2040 | 309 | ABC | OH_3p_type1 | L_3053_3055 | 3053 | 3055 | 1335 | B | UG_1p_type2
[6 empty] | L_2040_2041 | 2040 | 2041 | 383 | ABC | OH_3p_type1 | L_3055_3056 | 3055 | 3056 | 128 | B | UG_1p_type2
[6 empty] | L_2039_2042 | 2039 | 2042 | 35 | ABC | UG_3p_type2 | L_3056_3057 | 3056 | 3057 | 178 | B | UG_1p_type2
[6 empty] | L_2042_2043 | 2042 | 2043 | 158 | ABC | UG_3p_type2 | L_3057_3058 | 3057 | 3058 | 178 | B | UG_1p_type2
[6 empty] | L_2043_2044 | 2043 | 2044 | 342 | ABC | UG_3p_type2 | L_3058_3059 | 3058 | 3059 | 274 | B | UG_1p_type2
[6 empty] | L_2044_2045 | 2044 | 2045 | 323 | B | UG_1p_type2 | L_3059_3060 | 3059 | 3060 | 77 | B | UG_1p_type2
[6 empty] | L_2045_2046 | 2045 | 2046 | 330 | B | UG_1p_type2 | L_3060_3061 | 3060 | 3061 | 184 | B | UG_1p_type2
[6 empty] | L_2045_2047 | 2045 | 2047 | 189 | B | UG_1p_type2 | L_3055_3062 | 3055 | 3062 | 443 | B | UG_1p_type2
[6 empty] | L_2047_2048 | 2047 | 2048 | 259 | B | UG_1p_type2 | L_3062_3063 | 3062 | 3063 | 198 | B | UG_1p_type2
[6 empty] | L_2044_2049 | 2044 | 2049 | 130 | ABC | UG_3p_type2 | L_3063_3064 | 3063 | 3064 | 157 | B | UG_1p_type2
[6 empty] | L_2049_2050 | 2049 | 2050 | 124 | ABC | UG_3p_type2 | L_3064_3065 | 3064 | 3065 | 205 | B | UG_1p_type2
[6 empty] | L_2050_2051 | 2050 | 2051 | 139 | ABC | UG_3p_type2 | L_3065_3066 | 3065 | 3066 | 123 | B | UG_1p_type2
[6 empty] | L_2051_2052 | 2051 | 2052 | 134 | ABC | UG_3p_type2 | L_3066_3067 | 3066 | 3067 | 274 | B | UG_1p_type2
[6 empty] | L_2044_2053 | 2044 | 2053 | 464 | ABC | UG_3p_type2 | L_3030_3040 | 3030 | 3040 | 332 | ABC | OH_3p_type1
[6 empty] | L_2053_2054 | 2053 | 2054 | 139 | ABC | UG_3p_type2 | L_3040_3044 | 3040 | 3044 | 144 | C | OH_1p_type5
[6 empty] | L_2054_2055 | 2054 | 2055 | 156 | ABC | UG_3p_type2 | L_3044_3045 | 3044 | 3045 | 393 | C | OH_1p_type5
[6 empty] | L_2055_2056 | 2055 | 2056 | 204 | ABC | UG_3p_type2 | L_3040_3041 | 3040 | 3041 | 121 | C | OH_1p_type5
[6 empty] | L_2053_2057 | 2053 | 2057 | 761 | ABC | UG_3p_type2 | L_3041_3042 | 3041 | 3042 | 328 | C | OH_1p_type5
[6 empty] | L_2057_2058 | 2057 | 2058 | 407 | ABC | UG_3p_type2 | L_3042_3043 | 3042 | 3043 | 418 | C | OH_1p_type5
[6 empty] | L_2057_2059 | 2057 | 2059 | 685 | ABC | UG_3p_type2 | L_3040_3046 | 3040 | 3046 | 329 | ABC | OH_3p_type1
[6 empty] | L_2059_2060 | 2059 | 2060 | 304 | ABC | UG_3p_type2 | L_3046_3047 | 3046 | 3047 | 219 | ABC | OH_3p_type1
[12 empty] | L_3046_3048 | 3046 | 3048 | 130 | ABC | OH_3p_type1
[12 empty] | L_3048_3049 | 3048 | 3049 | 226 | ABC | OH_3p_type1
[12 empty] | L_3049_3050 | 3049 | 3050 | 167 | ABC | OH_3p_type1
[12 empty] | L_3050_3051 | 3050 | 3051 | 360 | ABC | OH_3p_type1
[12 empty] | L_3051_3052 | 3051 | 3052 | 292 | ABC | OH_3p_type1
[12 empty] | L_3030_3031 | 3030 | 3031 | 243 | ABC | OH_3p_type1
[12 empty] | L_3031_3032 | 3031 | 3032 | 251 | ABC | OH_3p_type1
[12 empty] | L_3032_3033 | 3032 | 3033 | 388 | ABC | OH_3p_type1
[12 empty] | L_3033_3034 | 3033 | 3034 | 257 | ABC | OH_3p_type1
[12 empty] | L_3034_3068 | 3034 | 3068 | 164 | ABC | OH_3p_type1
[12 empty] | L_3068_3069 | 3068 | 3069 | 329 | ABC | OH_3p_type1
[12 empty] | L_3069_3070 | 3069 | 3070 | 107 | ABC | UG_3p_type2
[12 empty] | L_3070_3071 | 3070 | 3071 | 141 | ABC | UG_3p_type2
[12 empty] | L_3071_3072 | 3071 | 3072 | 90 | ABC | UG_3p_type2
[12 empty] | L_3069_3073 | 3069 | 3073 | 20 | ABC | OH_3p_type1
[12 empty] | L_3073_3074 | 3073 | 3074 | 340 | ABC | OH_3p_type1
[12 empty] | L_3068_3075 | 3068 | 3075 | 188 | ABC | OH_3p_type1
[12 empty] | L_3076_3077 | 3076 | 3077 | 877 | ABC | OH_3p_type1
[12 empty] | L_3077_3078 | 3077 | 3078 | 80 | ABC | OH_3p_type1
[12 empty] | L_3076_3079 | 3076 | 3079 | 191 | ABC | OH_3p_type1
[12 empty] | L_3079_3080 | 3079 | 3080 | 604 | ABC | OH_3p_type1
[12 empty] | L_3080_3081 | 3080 | 3081 | 195 | ABC | OH_3p_type1
[12 empty] | L_3080_3082 | 3080 | 3082 | 540 | ABC | OH_3p_type1
[12 empty] | L_3082_3083 | 3082 | 3083 | 125 | A | UG_1p_type2
[12 empty] | L_3083_3084 | 3083 | 3084 | 196 | A | UG_1p_type2
[12 empty] | L_3084_3085 | 3084 | 3085 | 515 | A | UG_1p_type2
[12 empty] | L_3085_3086 | 3085 | 3086 | 338 | A | UG_1p_type2
[12 empty] | L_3086_3087 | 3086 | 3087 | 239 | A | UG_1p_type2
[12 empty] | L_3087_3088 | 3087 | 3088 | 420 | A | UG_1p_type2
[12 empty] | L_3088_3089 | 3088 | 3089 | 112 | A | UG_1p_type2
[12 empty] | L_3089_3090 | 3089 | 3090 | 565 | A | UG_1p_type2
[12 empty] | L_3090_3091 | 3090 | 3091 | 222 | A | UG_1p_type2
[12 empty] | L_3082_3092 | 3082 | 3092 | 185 | ABC | UG_3p_type2
[12 empty] | L_3092_3093 | 3092 | 3093 | 230 | A | UG_1p_type2
[12 empty] | L_3093_3094 | 3093 | 3094 | 125 | A | UG_1p_type2
[12 empty] | L_3094_3095 | 3094 | 3095 | 65 | A | UG_1p_type2
[12 empty] | L_3095_3096 | 3095 | 3096 | 296 | A | UG_1p_type2
[12 empty] | L_3096_3097 | 3096 | 3097 | 117 | A | UG_1p_type2
[12 empty] | L_3092_3098 | 3092 | 3098 | 284 | B | UG_1p_type2
[12 empty] | L_3098_3099 | 3098 | 3099 | 368 | B | UG_1p_type2
[12 empty] | L_3092_3100 | 3092 | 3100 | 91 | ABC | UG_3p_type2
[12 empty] | L_3100_3101 | 3100 | 3101 | 157 | C | UG_1p_type2
[12 empty] | L_3101_3102 | 3101 | 3102 | 225 | C | UG_1p_type2
[12 empty] | L_3102_3103 | 3102 | 3103 | 134 | C | UG_1p_type2
[12 empty] | L_3100_3104 | 3100 | 3104 | 223 | C | UG_1p_type2
[12 empty] | L_3104_3105 | 3104 | 3105 | 120 | C | UG_1p_type2
[12 empty] | L_3105_3106 | 3105 | 3106 | 181 | C | UG_1p_type2
[12 empty] | L_3082_3107 | 3082 | 3107 | 1461 | ABC | UG_3p_type1
[12 empty] | L_3107_3108 | 3107 | 3108 | 466 | A | UG_1p_type2
[12 empty] | L_3108_3109 | 3108 | 3109 | 136 | A | UG_1p_type2
[12 empty] | L_3109_3110 | 3109 | 3110 | 152 | A | UG_1p_type2
[12 empty] | L_3110_3111 | 3110 | 3111 | 276 | A | UG_1p_type2
[12 empty] | L_3111_3112 | 3111 | 3112 | 328 | A | UG_1p_type2
[12 empty] | L_3107_3113 | 3107 | 3113 | 245 | B | UG_1p_type2
[12 empty] | L_3113_3114 | 3113 | 3114 | 149 | B | UG_3p_type2
[12 empty] | L_3114_3115 | 3114 | 3115 | 331 | B | UG_1p_type2
[12 empty] | L_3113_3116 | 3113 | 3116 | 456 | B | UG_1p_type2
[12 empty] | L_3116_3117 | 3116 | 3117 | 112 | B | UG_1p_type2
[12 empty] | L_3107_3118 | 3107 | 3118 | 2267 | ABC | UG_3p_type1
[12 empty] | L_3118_3119 | 3118 | 3119 | 464 | B | UG_1p_type2
[12 empty] | L_3119_3120 | 3119 | 3120 | 350 | B | UG_1p_type2
[12 empty] | L_3120_3121 | 3120 | 3121 | 206 | B | UG_1p_type2
[12 empty] | L_3121_3122 | 3121 | 3122 | 177 | B | UG_1p_type2
[12 empty] | L_3119_3123 | 3119 | 3123 | 91 | B | UG_1p_type2
[12 empty] | L_3123_3124 | 3123 | 3124 | 67 | B | UG_1p_type2
[12 empty] | L_3124_3125 | 3124 | 3125 | 151 | B | UG_1p_type2
[12 empty] | L_3125_3126 | 3125 | 3126 | 343 | B | UG_1p_type2
[12 empty] | L_3126_3127 | 3126 | 3127 | 234 | B | UG_1p_type2
[12 empty] | L_3127_3128 | 3127 | 3128 | 238 | B | UG_1p_type2
[12 empty] | L_3128_3129 | 3128 | 3129 | 243 | B | UG_1p_type2
[12 empty] | L_3129_3130 | 3129 | 3130 | 230 | B | UG_1p_type2
[12 empty] | L_3130_3131 | 3130 | 3131 | 194 | B | UG_1p_type2
[12 empty] | L_3118_3132 | 3118 | 3132 | 501 | A | UG_1p_type2
[12 empty] | L_3132_3133 | 3132 | 3133 | 145 | A | UG_1p_type2
[12 empty] | L_3133_3134 | 3133 | 3134 | 281 | A | UG_1p_type2
[12 empty] | L_3134_3135 | 3134 | 3135 | 240 | A | UG_1p_type2
[12 empty] | L_3135_3136 | 3135 | 3136 | 367 | A | UG_1p_type2
[12 empty] | L_3133_3137 | 3133 | 3137 | 252 | A | UG_1p_type2
[12 empty] | L_3137_3138 | 3137 | 3138 | 351 | A | UG_1p_type2
[12 empty] | L_3138_3139 | 3138 | 3139 | 289 | A | UG_1p_type2
[12 empty] | L_3107_3140 | 3107 | 3140 | 255 | C | UG_1p_type2
[12 empty] | L_3140_3141 | 3140 | 3141 | 134 | C | UG_1p_type2
[12 empty] | L_3141_3142 | 3141 | 3142 | 193 | C | UG_1p_type2
[12 empty] | L_3142_3143 | 3142 | 3143 | 202 | C | UG_1p_type2
[12 empty] | L_3140_3148 | 3140 | 3148 | 147 | C | UG_1p_type2
[12 empty] | L_3148_3149 | 3148 | 3149 | 253 | C | UG_1p_type2
[12 empty] | L_3149_3150 | 3149 | 3150 | 139 | C | UG_1p_type2
[12 empty] | L_3150_3151 | 3150 | 3151 | 156 | C | UG_1p_type2
[12 empty] | L_3151_3152 | 3151 | 3152 | 260 | C | UG_1p_type2
[12 empty] | L_3152_3153 | 3152 | 3153 | 139 | C | UG_1p_type2
[12 empty] | L_3153_3154 | 3153 | 3154 | 119 | C | UG_1p_type2
[12 empty] | L_3154_3155 | 3154 | 3155 | 505 | C | UG_1p_type2
[12 empty] | L_3140_3156 | 3140 | 3156 | 319 | C | UG_1p_type2
[12 empty] | L_3156_3144 | 3156 | 3144 | 122 | C | UG_1p_type2
[12 empty] | L_3144_3145 | 3144 | 3145 | 178 | C | UG_1p_type2
[12 empty] | L_3145_3146 | 3145 | 3146 | 178 | C | UG_1p_type2
[12 empty] | L_3146_3147 | 3146 | 3147 | 178 | C | UG_1p_type2
[12 empty] | L_3156_3157 | 3156 | 3157 | 153 | C | UG_1p_type2
[12 empty] | L_3157_3158 | 3157 | 3158 | 295 | C | UG_1p_type2
[12 empty] | L_3158_3159 | 3158 | 3159 | 257 | C | UG_1p_type2
[12 empty] | L_3159_3160 | 3159 | 3160 | 243 | C | UG_1p_type2
[12 empty] | L_3160_3161 | 3160 | 3161 | 237 | C | UG_1p_type2
[12 empty] | L_3161_3162 | 3161 | 3162 | 176 | C | UG_1p_type2

## Line Configuration
Configuration 1: OH_3p_type1
Rmatrix (Ω/mile) | 0.61593 | 0.17093 | 0.17093
| 0.17093 | 0.61593 | 0.17093
| 0.17093 | 0.17093 | 0.61593
Xmatrix (Ω/mile) | 1.2094 | 0.43319 | 0.43319
| 0.43319 | 1.2094 | 0.43319
| 0.43319 | 0.43319 | 1.2094
Size | 4/0
Material | ACSR
Current Carrying Capacity (A) | 340
Resistance @ 25 °C (Ω/mile) | 0.445
Resistance @ 50 °C (Ω/mile) | 0.592
Geometric Mean Radisu (ft) | 0.00814
Conductor Diameter (in) | 0.563
Preferred Neutral | #2/0 ACSR 6/1
Construction | 1
Configuration 2: OH_2p_type2
Rmatrix (Ω/mile) | 0.58925 | 0.1695
| 0.1695 | 0.58925
Xmatrix (Ω/mile) | 1.0749 | 0.38788
| 0.38788 | 1.0749
Size | #4/0
Material | ACSR
Current Carrying Capacity (A) | 357
Resistance @ 25 °C (Ω/mile) | 0.41976
Resistance @ 50 °C (Ω/mile) | 0.62832
Geometric Mean Radisu (ft) | 0.0255
Conductor Diameter (in) | 0.502
Preferred Neutral | #2/0 ACSR 6/1
Construction | 2
Configuration 3: OH_1p_type2
Rmatrix (Ω/mile) | 0.59247
Xmatrix (Ω/mile) | 1.0658
Size | #4/0
Material | ACSR
Current Carrying Capacity (A) | 357
Resistance @ 25 °C (Ω/mile) | 0.41976
Resistance @ 50 °C (Ω/mile) | 0.62832
Geometric Mean Radisu (ft) | 0.0255
Conductor Diameter (in) | 0.502
Preferred Neutral | #2/0 ACSR 6/1
Construction | 2
Configuration 1: OH_3p_type5
Rmatrix (Ω/mile) | 1.1916 | 0.23485 | 0.23485
| 0.23485 | 1.1916 | 0.23485
| 0.23485 | 0.23485 | 1.1916
Xmatrix (Ω/mile) | 1.2095 | 0.48926 | 0.48926
| 0.48926 | 1.2095 | 0.48926
| 0.48926 | 0.48926 | 1.2095
Size | 1/0
Material | ACSR
Current Carrying Capacity (A) | 242
Resistance @ 25 °C (Ω/mile) | 0.95675
Resistance @ 50 °C (Ω/mile) | 1.0513
Geometric Mean Radisu (ft) | 0.012915
Conductor Diameter (in) | 0.398
Preferred Neutral | 1 ACSR 6/1
Construction | 1
Configuration 3: OH_1p_type5
Rmatrix (Ω/mile) | 1.1943
Xmatrix (Ω/mile) | 1.2054
Size | 1/0
Material | ACSR
Current Carrying Capacity (A) | 242
Resistance @ 25 °C (Ω/mile) | 0.95675
Resistance @ 50 °C (Ω/mile) | 1.0513
Geometric Mean Radisu (ft) | 0.012915
Conductor Diameter (in) | 0.398
Preferred Neutral | 1 ACSR 6/1
Construction | 1
Configuration 4: UG_3p_type1
Rmatrix (Ω/mile) | 1.0094 | 0.40973 | 0.40973
| 0.40973 | 1.0094 | 0.40973
| 0.40973 | 0.40973 | 1.0094
Xmatrix (Ω/mile) | 0.49316 | 0.10085 | 0.10085
| 0.10085 | 0.49316 | 0.10085
| 0.10085 | 0.10085 | 0.49316
Cmatrix (nF/mile) | 286.1016 | 0 | 0
| 0 | 286.1016 | 0
| 0 | 0 | 286.1016
Size | 4/0
Material | AA
Current Carrying Capacity of Conductor (A) | 326
Phase Conductor Resistance (Ω/1000 ft) | 0.105
Geometric Mean Radisu of Phase Conductor (ft) | 0.0167
Type Neutral | Concentric
Equivalent Resistance Concentric Neutral (Ω/1000 ft) | 0.3
Number of Strands | 11
Outside Diamter of Cable Including Neutral (in) | 1.218
Diameter Under Neutral (Over Screen) (in) | 1.09
Outside Diamter of Cable Insulation (Under Screen) (in) | 1.01
Diameter of Conductor (in) | 0.512
Dielectric Constant of Insulation | 2.75
Construction Type | 1
Configuration 5: UG_3p_type2
Rmatrix (Ω/mile) | 1.6926 | 0.55009 | 0.55009
| 0.55009 | 1.6926 | 0.55009
| 0.55009 | 0.55009 | 1.6926
Xmatrix (Ω/mile) | 0.79176 | 0.34493 | 0.34493
| 0.34493 | 0.79176 | 0.34493
| 0.34493 | 0.34493 | 0.79176
Cmatrix (nF/mile) | 207.8805 | 0 | 0
| 0 | 207.8805 | 0
| 0 | 0 | 207.8805
Size | 1/0
Material | AA
Current Carrying Capacity of Conductor (A) | 228
Phase Conductor Resistance (Ω/1000 ft) | 0.211
Geometric Mean Radisu of Phase Conductor (ft) | 0.111
Type Neutral | Concentric
Equivalent Resistance Concentric Neutral (Ω/1000 ft) | 0.55
Number of Strands | 6
Outside Diamter of Cable Including Neutral (in) | 1.068
Diameter Under Neutral (Over Screen) (in) | 0.94
Outside Diamter of Cable Insulation (Under Screen) (in) | 0.86
Diameter of Conductor (in) | 0.362
Dielectric Constant of Insulation | 2.75
Construction Type | 1
Configuration 6: UG_1p_type2
Rmatrix (Ω/mile) | 1.6753
Xmatrix (Ω/mile) | 1.21
Cmatrix (nF/mile) | 207.8805
Size | 1/0
Material | AA
Current Carrying Capacity of Conductor (A) | 228
Phase Conductor Resistance (Ω/1000 ft) | 0.211
Geometric Mean Radisu of Phase Conductor (ft) | 0.111
Type Neutral | Concentric
Equivalent Resistance Concentric Neutral (Ω/1000 ft) | 0.55
Number of Strands | 6
Outside Diamter of Cable Including Neutral (in) | 1.068
Diameter Under Neutral (Over Screen) (in) | 0.94
Outside Diamter of Cable Insulation (Under Screen) (in) | 0.86
Diameter of Conductor (in) | 0.362
Dielectric Constant of Insulation | 2.75
Construction Type | 1
OH Neutral:#2/0 ACSR 6/1
Size | 2/0
Material | ACSR
Current Carrying Capacity (A) | 270
Resistance @ 25 °C (Ω/mile) | 0.706
Resistance @ 50 °C (Ω/mile) | 0.895
Geometric Mean Radisu (ft) | 0.0051
Conductor Diameter (in) | 0.447
OH Neutral:1 ACSR 6/1
Size | 1
Material | ACSR
Current Carrying Capacity (A) | 212
Resistance @ 25 °C (Ω/mile) | 1.1816
Resistance @ 50 °C (Ω/mile) | 1.2983
Geometric Mean Radisu (ft) | 0.011487
Conductor Diameter (in) | 0.354
Construction Type: 1 | GMDP (in) | GMDPN (in)
3 phase -OH | 58.6 | 53.6
V phase -OH | 88 | 55.8
Single phase - OH | 51 | 51
UG All phase | 5.4288 | 0
Construction Type: 2 | GMDP (in) | GMDPN (in)
3 phase -OH | 58.6 | 53.6
V phase -OH | 88 | 55.8
Single phase - OH | 51 | 51
UG All phase | 3 | 0

## Distribution Transformer
Three-phase Secondary Distribution Transformers
Name | Connection | Bus of Winding 1 | Bus of Winding 2 | Primary voltage rating (kV) | Secondary voltage rating (kV) | kVA rating (kVA) | %R | %X
T_1003 | Grd. Y - Grd. Y | bus1003 | T_bus1003_L | 13.8 | 0.208 | 112.5 | 2.43 | 3.87
T_1004 | Grd. Y - Grd. Y | bus1004 | T_bus1004_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_1005 | Grd. Y - Grd. Y | bus1005 | T_bus1005_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_1008 | Grd. Y - Grd. Y | bus1008 | T_bus1008_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_1009 | Grd. Y - Grd. Y | bus1009 | T_bus1009_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_1010 | Grd. Y - Grd. Y | bus1010 | T_bus1010_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_1013 | Grd. Y - Grd. Y | bus1013 | T_bus1013_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2002 | Grd. Y - Grd. Y | bus2002 | T_bus2002_L | 13.8 | 0.208 | 300 | 1.8 | 4.5
T_2003 | Grd. Y - Grd. Y | bus2003 | T_bus2003_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2005 | Grd. Y - Grd. Y | bus2005 | T_bus2005_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2010 | Grd. Y - Grd. Y | bus2010 | T_bus2010_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2011 | Grd. Y - Grd. Y | bus2011 | T_bus2011_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2029 | Grd. Y - Grd. Y | bus2029 | T_bus2029_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2030 | Grd. Y - Grd. Y | bus2030 | T_bus2030_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2032 | Grd. Y - Grd. Y | bus2032 | T_bus2032_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2034 | Grd. Y - Grd. Y | bus2034 | T_bus2034_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2035 | Grd. Y - Grd. Y | bus2035 | T_bus2035_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2037 | Grd. Y - Grd. Y | bus2037 | T_bus2037_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2040 | Grd. Y - Grd. Y | bus2040 | T_bus2040_L | 13.8 | 0.208 | 300 | 1.8 | 4.5
T_2041 | Grd. Y - Grd. Y | bus2041 | T_bus2041_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_2042 | Grd. Y - Grd. Y | bus2042 | T_bus2042_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2043 | Grd. Y - Grd. Y | bus2043 | T_bus2043_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_2052 | Grd. Y - Grd. Y | bus2052 | T_bus2052_L | 13.8 | 0.208 | 225 | 2.2 | 4.65
T_2053 | Grd. Y - Grd. Y | bus2053 | T_bus2053_L | 13.8 | 0.208 | 225 | 2.2 | 4.65
T_2058 | Grd. Y - Grd. Y | bus2058 | T_bus2058_L | 13.8 | 0.208 | 300 | 1.8 | 4.5
T_3002 | Grd. Y - Grd. Y | bus3002 | T_bus3002_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3004 | Grd. Y - Grd. Y | bus3004 | T_bus3004_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3006 | Grd. Y - Grd. Y | bus3006 | T_bus3006_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3007 | Grd. Y - Grd. Y | bus3007 | T_bus3007_L | 13.8 | 0.208 | 75 | 2.27 | 1.91
T_3031 | Grd. Y - Grd. Y | bus3031 | T_bus3031_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3032 | Grd. Y - Grd. Y | bus3032 | T_bus3032_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3033 | Grd. Y - Grd. Y | bus3033 | T_bus3033_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3034 | Grd. Y - Grd. Y | bus3034 | T_bus3034_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3035 | Grd. Y - Grd. Y | bus3035 | T_bus3035_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3036 | Grd. Y - Grd. Y | bus3036 | T_bus3036_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3037 | Grd. Y - Grd. Y | bus3037 | T_bus3037_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3038 | Grd. Y - Grd. Y | bus3038 | T_bus3038_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3039 | Grd. Y - Grd. Y | bus3039 | T_bus3039_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3047 | Grd. Y - Grd. Y | bus3047 | T_bus3047_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3048 | Grd. Y - Grd. Y | bus3048 | T_bus3048_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3049 | Grd. Y - Grd. Y | bus3049 | T_bus3049_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3050 | Grd. Y - Grd. Y | bus3050 | T_bus3050_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3051 | Grd. Y - Grd. Y | bus3051 | T_bus3051_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3052 | Grd. Y - Grd. Y | bus3052 | T_bus3052_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3054 | Grd. Y - Grd. Y | bus3054 | T_bus3054_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3070 | Grd. Y - Grd. Y | bus3070 | T_bus3070_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3071 | Grd. Y - Grd. Y | bus3071 | T_bus3071_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3072 | Grd. Y - Grd. Y | bus3072 | T_bus3072_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3073 | Grd. Y - Grd. Y | bus3073 | T_bus3073_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3074 | Grd. Y - Grd. Y | bus3074 | T_bus3074_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3077 | Grd. Y - Grd. Y | bus3077 | T_bus3077_L | 13.8 | 0.208 | 500 | 1.6 | 5.9
T_3078 | Grd. Y - Grd. Y | bus3078 | T_bus3078_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
T_3081 | Grd. Y - Grd. Y | bus3081 | T_bus3081_L | 13.8 | 0.208 | 45 | 2.52 | 1.73
Single-phase Secondary Distribution Transformers
Name | Connection | Phases | Bus of Winding 1 | Bus of Winding 2 | Primary voltage rating (kV) | Secondary voltage rating (kV) | kVA rating (kVA) | %R | %X
T_1006 | Delta - Delta | AB | bus1006 | T_bus1006_L | 13.8 | 0.208 | 75 | 1 | 2.1
T_1007 | Delta - Delta | AB | bus1007 | T_bus1007_L | 13.8 | 0.208 | 25 | 1.33 | 1.88
Single-Phase Center-tapped Secondary Distribution Transformer
Name | Bus of Winding 1 | Phase | Voltage rating of Winding 1 (kV) | kVA rating of Winding 1 (kVA) | Bus of Winding 2 | Phase | Voltage rating of Winding 2 (kV) | kVA rating of Winding 2 (kVA) | Bus of Winding 3 | Phase | Voltage rating of Winding 3 (kV) | kVA rating of Winding 3 (kVA) | %R1 | %R2 | %R3 | %X12 | %X13 | %X23
T_1011 | bus1011 | A | 7.9677 | 25 | T_bus1011_L | a | 0.12 | 25 | T_bus1011_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_1012 | bus1012 | B | 7.9677 | 37.5 | T_bus1012_L | a | 0.12 | 37.5 | T_bus1012_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_1014 | bus1014 | B | 7.9677 | 25 | T_bus1014_L | a | 0.12 | 25 | T_bus1014_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_1015 | bus1015 | B | 7.9677 | 25 | T_bus1015_L | a | 0.12 | 25 | T_bus1015_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_1016 | bus1016 | C | 7.9677 | 50 | T_bus1016_L | a | 0.12 | 50 | T_bus1016_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_1017 | bus1017 | C | 7.9677 | 37.5 | T_bus1017_L | a | 0.12 | 37.5 | T_bus1017_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2008 | bus2008 | A | 7.9677 | 25 | T_bus2008_L | a | 0.12 | 25 | T_bus2008_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2009 | bus2009 | A | 7.9677 | 25 | T_bus2009_L | a | 0.12 | 25 | T_bus2009_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2014 | bus2014 | B | 7.9677 | 37.5 | T_bus2014_L | a | 0.12 | 37.5 | T_bus2014_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2015 | bus2015 | B | 7.9677 | 25 | T_bus2015_L | a | 0.12 | 25 | T_bus2015_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2016 | bus2016 | B | 7.9677 | 25 | T_bus2016_L | a | 0.12 | 25 | T_bus2016_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2017 | bus2017 | B | 7.9677 | 25 | T_bus2017_L | a | 0.12 | 25 | T_bus2017_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2018 | bus2018 | B | 7.9677 | 25 | T_bus2018_L | a | 0.12 | 25 | T_bus2018_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2020 | bus2020 | B | 7.9677 | 25 | T_bus2020_L | a | 0.12 | 25 | T_bus2020_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2022 | bus2022 | C | 7.9677 | 25 | T_bus2022_L | a | 0.12 | 25 | T_bus2022_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2023 | bus2023 | C | 7.9677 | 15 | T_bus2023_L | a | 0.12 | 15 | T_bus2023_L | b | 0.12 | 15 | 0.83 | 1.66 | 1.66 | 1.536 | 1.536 | 1.024
T_2024 | bus2024 | C | 7.9677 | 25 | T_bus2024_L | a | 0.12 | 25 | T_bus2024_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2025 | bus2025 | C | 7.9677 | 25 | T_bus2025_L | a | 0.12 | 25 | T_bus2025_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2028 | bus2028 | A | 7.9677 | 25 | T_bus2028_L | a | 0.12 | 25 | T_bus2028_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2031 | bus2031 | A | 7.9677 | 25 | T_bus2031_L | a | 0.12 | 25 | T_bus2031_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2045 | bus2045 | B | 7.9677 | 15 | T_bus2045_L | a | 0.12 | 15 | T_bus2045_L | b | 0.12 | 15 | 0.83 | 1.66 | 1.66 | 1.536 | 1.536 | 1.024
T_2046 | bus2046 | B | 7.9677 | 50 | T_bus2046_L | a | 0.12 | 50 | T_bus2046_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_2047 | bus2047 | B | 7.9677 | 50 | T_bus2047_L | a | 0.12 | 50 | T_bus2047_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_2048 | bus2048 | B | 7.9677 | 50 | T_bus2048_L | a | 0.12 | 50 | T_bus2048_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_2049 | bus2049 | C | 7.9677 | 37.5 | T_bus2049_L | a | 0.12 | 37.5 | T_bus2049_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2050 | bus2050 | C | 7.9677 | 37.5 | T_bus2050_L | a | 0.12 | 37.5 | T_bus2050_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2051 | bus2051 | C | 7.9677 | 37.5 | T_bus2051_L | a | 0.12 | 37.5 | T_bus2051_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2054 | bus2054 | A | 7.9677 | 37.5 | T_bus2054_L | a | 0.12 | 37.5 | T_bus2054_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_2055 | bus2055 | A | 7.9677 | 50 | T_bus2055_L | a | 0.12 | 50 | T_bus2055_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_2056 | bus2056 | A | 7.9677 | 25 | T_bus2056_L | a | 0.12 | 25 | T_bus2056_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2059 | bus2059 | B | 7.9677 | 25 | T_bus2059_L | a | 0.12 | 25 | T_bus2059_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_2060 | bus2060 | B | 7.9677 | 25 | T_bus2060_L | a | 0.12 | 25 | T_bus2060_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3009 | bus3009 | A | 7.9677 | 37.5 | T_bus3009_L | a | 0.12 | 37.5 | T_bus3009_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3010 | bus3010 | A | 7.9677 | 37.5 | T_bus3010_L | a | 0.12 | 37.5 | T_bus3010_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3011 | bus3011 | A | 7.9677 | 37.5 | T_bus3011_L | a | 0.12 | 37.5 | T_bus3011_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3012 | bus3012 | A | 7.9677 | 50 | T_bus3012_L | a | 0.12 | 50 | T_bus3012_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3013 | bus3013 | B | 7.9677 | 25 | T_bus3013_L | a | 0.12 | 25 | T_bus3013_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3014 | bus3014 | B | 7.9677 | 37.5 | T_bus3014_L | a | 0.12 | 37.5 | T_bus3014_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3016 | bus3016 | B | 7.9677 | 37.5 | T_bus3016_L | a | 0.12 | 37.5 | T_bus3016_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3017 | bus3017 | B | 7.9677 | 100 | T_bus3017_L | a | 0.12 | 100 | T_bus3017_L | b | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3018 | bus3018 | C | 7.9677 | 37.5 | T_bus3018_L | a | 0.12 | 37.5 | T_bus3018_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3019 | bus3019 | C | 7.9677 | 37.5 | T_bus3019_L | a | 0.12 | 37.5 | T_bus3019_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3020 | bus3020 | C | 7.9677 | 100 | T_bus3020_L | a | 0.12 | 100 | T_bus3020_L | b | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3021 | bus3021 | C | 7.9677 | 37.5 | T_bus3021_L | a | 0.12 | 37.5 | T_bus3021_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3023 | bus3023 | A | 7.9677 | 50 | T_bus3023_L | a | 0.12 | 50 | T_bus3023_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3024 | bus3024 | A | 7.9677 | 37.5 | T_bus3024_L | a | 0.12 | 37.5 | T_bus3024_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3025 | bus3025 | A | 7.9677 | 50 | T_bus3025_L | a | 0.12 | 50 | T_bus3025_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3026 | bus3026 | A | 7.9677 | 37.5 | T_bus3026_L | a | 0.12 | 37.5 | T_bus3026_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3027 | bus3027 | A | 7.9677 | 100 | T_bus3027_L | a | 0.12 | 100 | T_bus3027_L | b | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3028 | bus3028 | A | 7.9677 | 100 | T_bus3028_L | a | 0.12 | 100 | T_bus3028_L | b | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3029 | bus3029 | A | 7.9677 | 37.5 | T_bus3029_L | a | 0.12 | 37.5 | T_bus3029_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3041 | bus3041 | C | 7.9677 | 50 | T_bus3041_L | a | 0.12 | 50 | T_bus3041_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3042 | bus3042 | C | 7.9677 | 37.5 | T_bus3042_L | a | 0.12 | 37.5 | T_bus3042_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3043 | bus3043 | C | 7.9677 | 37.5 | T_bus3043_L | a | 0.12 | 37.5 | T_bus3043_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3044 | bus3044 | C | 7.9677 | 37.5 | T_bus3044_L | a | 0.12 | 37.5 | T_bus3044_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3045 | bus3045 | C | 7.9677 | 37.5 | T_bus3045_L | a | 0.12 | 37.5 | T_bus3045_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3056 | bus3056 | B | 7.9677 | 37.5 | T_bus3056_L | a | 0.12 | 37.5 | T_bus3056_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3057 | bus3057 | B | 7.9677 | 37.5 | T_bus3057_L | a | 0.12 | 37.5 | T_bus3057_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3058 | bus3058. | B | 7.9677 | 37.5 | T_bus3058_L | a | 0.12 | 37.5 | T_bus3058_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3059 | bus3059 | B | 7.9677 | 37.5 | T_bus3059_L | a | 0.12 | 37.5 | T_bus3059_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3060 | bus3060 | B | 7.9677 | 37.5 | T_bus3060_L | a | 0.12 | 37.5 | T_bus3060_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3061 | bus3061 | B | 7.9677 | 37.5 | T_bus3061_L | a | 0.12 | 37.5 | T_bus3061_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3062 | bus3062 | B | 7.9677 | 37.5 | T_bus3062_L | a | 0.12 | 37.5 | T_bus3062_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3063 | bus3063 | B | 7.9677 | 37.5 | T_bus3063_L | a | 0.12 | 37.5 | T_bus3063_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3064 | bus3064 | B | 7.9677 | 37.5 | T_bus3064_L | a | 0.12 | 37.5 | T_bus3064_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3065 | bus3065 | B | 7.9677 | 37.5 | T_bus3065_L | a | 0.12 | 37.5 | T_bus3065_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3066 | bus3066 | B | 7.9677 | 37.5 | T_bus3066_L | a | 0.12 | 37.5 | T_bus3066_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3067 | bus3067 | B | 7.9677 | 37.5 | T_bus3067_L | a | 0.12 | 37.5 | T_bus3067_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3083 | bus3083 | A | 7.9677 | 37.5 | T_bus3083_L | a | 0.12 | 37.5 | T_bus3083_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3084 | bus3084 | A | 7.9677 | 37.5 | T_bus3084_L | a | 0.12 | 37.5 | T_bus3084_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3085 | bus3085 | A | 7.9677 | 37.5 | T_bus3085_L | a | 0.12 | 37.5 | T_bus3085_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3086 | bus3086 | A | 7.9677 | 37.5 | T_bus3086_L | a | 0.12 | 37.5 | T_bus3086_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3087 | bus3087 | A | 7.9677 | 37.5 | T_bus3087_L | a | 0.12 | 37.5 | T_bus3087_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3088 | bus3088 | A | 7.9677 | 37.5 | T_bus3088_L | a | 0.12 | 37.5 | T_bus3088_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3089 | bus3089 | A | 7.9677 | 37.5 | T_bus3089_L | a | 0.12 | 37.5 | T_bus3089_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3090 | bus3090 | A | 7.9677 | 37.5 | T_bus3090_L | a | 0.12 | 37.5 | T_bus3090_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3091 | bus3091 | A | 7.9677 | 25 | T_bus3091_L | a | 0.12 | 25 | T_bus3091_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3093 | bus3093 | A | 7.9677 | 37.5 | T_bus3093_L | a | 0.12 | 37.5 | T_bus3093_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3094 | bus3094 | A | 7.9677 | 37.5 | T_bus3094_L | a | 0.12 | 37.5 | T_bus3094_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3095 | bus3095 | A | 7.9677 | 37.5 | T_bus3095_L | a | 0.12 | 37.5 | T_bus3095_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3096 | bus3096 | A | 7.9677 | 37.5 | T_bus3096_L | a | 0.12 | 37.5 | T_bus3096_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3097 | bus3097 | A | 7.9677 | 37.5 | T_bus3097_L | a | 0.12 | 37.5 | T_bus3097_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3098 | bus3098 | B | 7.9677 | 50 | T_bus3098_L | a | 0.12 | 50 | T_bus3098_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3099 | bus3099 | B | 7.9677 | 37.5 | T_bus3099_L | a | 0.12 | 37.5 | T_bus3099_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3101 | bus3101 | C | 7.9677 | 37.5 | T_bus3101_L | a | 0.12 | 37.5 | T_bus3101_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3102 | bus3102 | C | 7.9677 | 37.5 | T_bus3102_L | a | 0.12 | 37.5 | T_bus3102_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3103 | bus3103 | C | 7.9677 | 50 | T_bus3103_L | a | 0.12 | 50 | T_bus3103_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3104 | bus3104 | C | 7.9677 | 100 | T_bus3104_L | a | 0.12 | 100 | T_bus3104_L | b | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3105 | bus3105 | C | 7.9677 | 37.5 | T_bus3105_L | a | 0.12 | 37.5 | T_bus3105_L. | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3106 | bus3106 | C | 7.9677 | 100 | T_bus3106_L | a | 0.12 | 100 | T_bus3106_L | b | 0.12 | 100 | 0.56 | 1.12 | 1.12 | 2.688 | 2.688 | 1.792
T_3108 | bus3108 | A | 7.9677 | 37.5 | T_bus3108_L | a | 0.12 | 37.5 | T_bus3108_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3109 | bus3109 | A | 7.9677 | 37.5 | T_bus3109_L | a | 0.12 | 37.5 | T_bus3109_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3110 | bus3110 | A | 7.9677 | 50 | T_bus3110_L | a | 0.12 | 50 | T_bus3110_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3111 | bus3111 | A | 7.9677 | 50 | T_bus3111_L | a | 0.12 | 50 | T_bus3111_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3112 | bus3112 | A | 7.9677 | 50 | T_bus3112_L | a | 0.12 | 50 | T_bus3112_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3114 | bus3114 | B | 7.9677 | 37.5 | T_bus3114_L | a | 0.12 | 37.5 | T_bus3114_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3115 | bus3115 | B | 7.9677 | 50 | T_bus3115_L | a | 0.12 | 50 | T_bus3115_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3116 | bus3116 | B | 7.9677 | 37.5 | T_bus3116_L | a | 0.12 | 37.5 | T_bus3116_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3117 | bus3117 | B | 7.9677 | 37.5 | T_bus3117_L | a | 0.12 | 37.5 | T_bus3117_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3120 | bus3120 | B | 7.9677 | 37.5 | T_bus3120_L | a | 0.12 | 37.5 | T_bus3120_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3121 | bus3121 | B | 7.9677 | 37.5 | T_bus3121_L | a | 0.12 | 37.5 | T_bus3121_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3122 | bus3122 | B | 7.9677 | 37.5 | T_bus3122_L | a | 0.12 | 37.5 | T_bus3122_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3123 | bus3123 | B | 7.9677 | 37.5 | T_bus3123_L | a | 0.12 | 37.5 | T_bus3123_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3124 | bus3124 | B | 7.9677 | 37.5 | T_bus3124_L | a | 0.12 | 37.5 | T_bus3124_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3125 | bus3125 | B | 7.9677 | 15 | T_bus3125_L | a | 0.12 | 15 | T_bus3125_L | b | 0.12 | 15 | 0.83 | 1.66 | 1.66 | 1.536 | 1.536 | 1.024
T_3126 | bus3126 | B | 7.9677 | 37.5 | T_bus3126_L | a | 0.12 | 37.5 | T_bus3126_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3127 | bus3127 | B | 7.9677 | 37.5 | T_bus3127_L | a | 0.12 | 37.5 | T_bus3127_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3128 | bus3128 | B | 7.9677 | 37.5 | T_bus3128_L | a | 0.12 | 37.5 | T_bus3128_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3129 | bus3129 | B | 7.9677 | 37.5 | T_bus3129_L | a | 0.12 | 37.5 | T_bus3129_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3130 | bus3130 | B | 7.9677 | 37.5 | T_bus3130_L | a | 0.12 | 37.5 | T_bus3130_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3131 | bus3131 | B | 7.9677 | 37.5 | T_bus3131_L | a | 0.12 | 37.5 | T_bus3131_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3132 | bus3132 | A | 7.9677 | 50 | T_bus3132_L | a | 0.12 | 50 | T_bus3132_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3134 | bus3134 | A | 7.9677 | 50 | T_bus3134_L | a | 0.12 | 50 | T_bus3134_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3135 | bus3135 | A | 7.9677 | 37.5 | T_bus3135_L | a | 0.12 | 37.5 | T_bus3135_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3136 | bus3136 | A | 7.9677 | 50 | T_bus3136_L | a | 0.12 | 50 | T_bus3136_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3137 | bus3137 | A | 7.9677 | 50 | T_bus3137_L | a | 0.12 | 50 | T_bus3137_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3138 | bus3138 | A | 7.9677 | 50 | T_bus3138_L | a | 0.12 | 50 | T_bus3138_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3139 | bus3139 | A | 7.9677 | 37.5 | T_bus3139_L | a | 0.12 | 37.5 | T_bus3139_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3141 | bus3141 | C | 7.9677 | 37.5 | T_bus3141_L | a | 0.12 | 37.5 | T_bus3141_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3142 | bus3142 | C | 7.9677 | 37.5 | T_bus3142_L | a | 0.12 | 37.5 | T_bus3142_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3143 | bus3143 | C | 7.9677 | 37.5 | T_bus3143_L | a | 0.12 | 37.5 | T_bus3143_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3144 | bus3144 | C | 7.9677 | 15 | T_bus3144_L | a | 0.12 | 15 | T_bus3144_L | b | 0.12 | 15 | 0.83 | 1.66 | 1.66 | 1.536 | 1.536 | 1.024
T_3145 | bus3145 | C | 7.9677 | 37.5 | T_bus3145_L | a | 0.12 | 37.5 | T_bus3145_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3146 | bus3146 | C | 7.9677 | 37.5 | T_bus3146_L | a | 0.12 | 37.5 | T_bus3146_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3147 | bus3147 | C | 7.9677 | 37.5 | T_bus3147_L | a | 0.12 | 37.5 | T_bus3147_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3148 | bus3148 | C | 7.9677 | 50 | T_bus3148_L | a | 0.12 | 50 | T_bus3148_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3149 | bus3149 | C | 7.9677 | 37.5 | T_bus3149_L | a | 0.12 | 37.5 | T_bus3149_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3150 | bus3150 | C | 7.9677 | 25 | T_bus3150_L | a | 0.12 | 25 | T_bus3150_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3151 | bus3151 | C | 7.9677 | 25 | T_bus3151_L | a | 0.12 | 25 | T_bus3151_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3152 | bus3152 | C | 7.9677 | 25 | T_bus3152_L | a | 0.12 | 25 | T_bus3152_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3153 | bus3153 | C | 7.9677 | 37.5 | T_bus3153_L | a | 0.12 | 37.5 | T_bus3153_L | b | 0.12 | 37.5 | 0.595 | 1.19 | 1.19 | 2.076 | 2.076 | 1.384
T_3154 | bus3154 | C | 7.9677 | 25 | T_bus3154_L | a | 0.12 | 25 | T_bus3154_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3155 | bus3155 | C | 7.9677 | 25 | T_bus3155_L | a | 0.12 | 25 | T_bus3155_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3157 | bus3157 | C | 7.9677 | 50 | T_bus3157_L | a | 0.12 | 50 | T_bus3157_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3158 | bus3158 | C | 7.9677 | 50 | T_bus3158_L | a | 0.12 | 50 | T_bus3158_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3159 | bus3159 | C | 7.9677 | 50 | T_bus3159_L | a | 0.12 | 50 | T_bus3159_L | b | 0.12 | 50 | 0.55 | 1.1 | 1.1 | 2.16 | 2.16 | 1.44
T_3160 | bus3160 | C | 7.9677 | 25 | T_bus3160_L | a | 0.12 | 25 | T_bus3160_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3161 | bus3161 | C | 7.9677 | 25 | T_bus3161_L | a | 0.12 | 25 | T_bus3161_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
T_3162 | bus3162 | C | 7.9677 | 25 | T_bus3162_L | a | 0.12 | 25 | T_bus3162_L | b | 0.12 | 25 | 0.665 | 1.33 | 1.33 | 2.256 | 2.256 | 1.504
Note: The impedance parameters of single-phase center-tapped transformers are calculated using equation (1) in [1]. [1] W. H. Kersting, “Center-Tapped Transformer and 120-/240-V Secondary Models,” IEEE Trans. Ind. Appl., vol. 45, pp. 575–581, Mar./Apr. 2009.

## Circuit Breakers
Three-Phase Circuit Breakers
Name | Bus A | Bus B | Positive‐sequence resistance (Ω/foot) | Zero-sequence resistance (Ω/foot) | Positive‐sequence reactance (Ω/foot) | Zero-sequence reactance (Ω/foot) | Positive‐sequence capacitance (nF/foot) | Zero‐sequence capacitance (nF/foot) | Normal Status
CB_101 | bus1 | bus1001 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_102 | bus1010 | bus2057 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Open
CB_201 | bus1 | bus2001 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_202 | bus2012 | bus2013 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_203 | bus2021 | bus2026 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_204 | bus2013 | bus3005 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Open
CB_301 | bus1 | bus3001 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_302 | bus3075 | bus3076 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Closed
CB_303 | bus3081 | bus2016 | 0.0001 | 0.0001 | 0 | 0 | 0 | 0 | Open

## Capacitor Banks
Three-Phase Shunt Capacitor Bank
Name | Bus | kV Rating (kV) | Connection | kVAr rating (kVAr) | Normal Status
CAP_201 | bus2038 | 13.8 | wye - Grd. | 50 | Closed
CAP_301 | bus3079 | 13.8 | wye - Grd. | 50 | Closed

## Load Configuration
Note: For the loads connected to single-phase center-tapped transformers, 1. The loads are defined as two 120V loads connected line to neutral. 2. Phase designation "AB" implies two 120V loads. 3. kW load is divided equally between the two 120V "phases".
Spot Loads Configuration
Load Name | Number of phases | Bus | Phases | Voltage (V) | Connection & Load Model
Load_1003 | 3 | T_bus1003_L | ABC | 208 | wye-PQ
Load_1004 | 3 | T_bus1004_L | ABC | 208 | wye-PQ
Load_1005 | 3 | T_bus1005_L | ABC | 208 | wye-PQ
Load_1006 | 2 | T_b6us1006_L | AB | 208 | delta-PQ
Load_1007 | 2 | T_bu7s1007_L | AB | 208 | delta-PQ
Load_1008 | 3 | T_bus1008_L | ABC | 208 | wye-PQ
Load_1009 | 3 | T_bus1009_L | ABC | 208 | wye-PQ
Load_1010 | 3 | T_bus1010_L | ABC | 208 | wye-PQ
Load_1011 | 2 | T_bus1011_L | AB | 120 | wye-PQ
Load_1012 | 2 | T_bus1012_L | AB | 120 | wye-PQ
Load_1013 | 3 | T_bus1013_L | ABC | 208 | wye-PQ
Load_1014 | 2 | T_bus1014_L | AB | 120 | wye-PQ
Load_1015 | 2 | T_bus1015_L | AB | 120 | wye-PQ
Load_1016 | 2 | T_bus1016_L | AB | 120 | wye-PQ
Load_1017 | 2 | T_bus1017_L | AB | 120 | wye-PQ
Load_2002 | 3 | T_bus2002_L | ABC | 208 | wye-PQ
Load_2003 | 3 | T_bus2003_L | ABC | 208 | wye-PQ
Load_2005 | 3 | T_bus2005_L | ABC | 208 | wye-PQ
Load_2008 | 2 | T_bus2008_L | AB | 120 | wye-PQ
Load_2009 | 2 | T_bus2009_L | AB | 120 | wye-PQ
Load_2010 | 3 | T_bus2010_L | ABC | 208 | wye-PQ
Load_2011 | 3 | T_bus2011_L | ABC | 208 | wye-PQ
Load_2014 | 2 | T_bus2014_L | AB | 120 | wye-PQ
Load_2015 | 2 | T_bus2015_L | AB | 120 | wye-PQ
Load_2016 | 2 | T_bus2016_L | AB | 120 | wye-PQ
Load_2017 | 2 | T_bus2017_L | AB | 120 | wye-PQ
Load_2018 | 2 | T_bus2018_L | AB | 120 | wye-PQ
Load_2020 | 2 | T_bus2020_L | AB | 120 | wye-PQ
Load_2022 | 2 | T_bus2022_L | AB | 120 | wye-PQ
Load_2023 | 2 | T_bus2023_L | AB | 120 | wye-PQ
Load_2024 | 2 | T_bus2024_L | AB | 120 | wye-PQ
Load_2025 | 2 | T_bus2025_L | AB | 120 | wye-PQ
Load_2028 | 2 | T_bus2028_L | AB | 120 | wye-PQ
Load_2029 | 3 | T_bus2029_L | ABC | 208 | wye-PQ
Load_2030 | 3 | T_bus2030_L | ABC | 208 | wye-PQ
Load_2031 | 2 | T_bus2031_L | AB | 120 | wye-PQ
Load_2032 | 3 | T_bus2032_L | ABC | 208 | wye-PQ
Load_2034 | 3 | T_bus2034_L | ABC | 208 | wye-PQ
Load_2035 | 3 | T_bus2035_L | ABC | 208 | wye-PQ
Load_2037 | 3 | T_bus2037_L | ABC | 208 | wye-PQ
Load_2040 | 3 | T_bus2040_L | ABC | 208 | wye-PQ
Load_2041 | 3 | T_bus2041_L | ABC | 208 | wye-PQ
Load_2042 | 3 | T_bus2042_L | ABC | 208 | wye-PQ
Load_2043 | 3 | T_bus2043_L | ABC | 208 | wye-PQ
Load_2045 | 2 | T_bus2045_L | AB | 120 | wye-PQ
Load_2046 | 2 | T_bus2046_L | AB | 120 | wye-PQ
Load_2047 | 2 | T_bus2047_L | AB | 120 | wye-PQ
Load_2048 | 2 | T_bus2048_L | AB | 120 | wye-PQ
Load_2049 | 2 | T_bus2049_L | AB | 120 | wye-PQ
Load_2050 | 2 | T_bus2050_L | AB | 120 | wye-PQ
Load_2051 | 2 | T_bus2051_L | AB | 120 | wye-PQ
Load_2052 | 3 | T_bus2052_L | ABC | 208 | wye-PQ
Load_2053 | 3 | T_bus2053_L | ABC | 208 | wye-PQ
Load_2054 | 2 | T_bus2054_L | AB | 120 | wye-PQ
Load_2055 | 2 | T_bus2055_L | AB | 120 | wye-PQ
Load_2056 | 2 | T_bus2056_L | AB | 120 | wye-PQ
Load_2058 | 3 | T_bus2058_L | ABC | 208 | wye-PQ
Load_2059 | 2 | T_bus2059_L | AB | 120 | wye-PQ
Load_2060 | 2 | T_bus2060_L | AB | 120 | wye-PQ
Load_3002 | 3 | T_bus3002_L | ABC | 208 | wye-PQ
Load_3004 | 3 | T_bus3004_L | ABC | 208 | wye-PQ
Load_3006 | 3 | T_bus3006_L | ABC | 208 | wye-PQ
Load_3007 | 3 | T_bus3007_L | ABC | 208 | wye-PQ
Load_3009 | 2 | T_bus3009_L | AB | 120 | wye-PQ
Load_3010 | 2 | T_bus3010_L | AB | 120 | wye-PQ
Load_3011 | 2 | T_bus3011_L | AB | 120 | wye-PQ
Load_3012 | 2 | T_bus3012_L | AB | 120 | wye-PQ
Load_3013 | 2 | T_bus3013_L | AB | 120 | wye-PQ
Load_3014 | 2 | T_bus3014_L | AB | 120 | wye-PQ
Load_3016 | 2 | T_bus3016_L | AB | 120 | wye-PQ
Load_3017 | 2 | T_bus3017_L | AB | 120 | wye-PQ
Load_3018 | 2 | T_bus3018_L | AB | 120 | wye-PQ
Load_3019 | 2 | T_bus3019_L | AB | 120 | wye-PQ
Load_3020 | 2 | T_bus3020_L | AB | 120 | wye-PQ
Load_3021 | 2 | T_bus3021_L | AB | 120 | wye-PQ
Load_3023 | 2 | T_bus3023_L | AB | 120 | wye-PQ
Load_3024 | 2 | T_bus3024_L | AB | 120 | wye-PQ
Load_3025 | 2 | T_bus3025_L | AB | 120 | wye-PQ
Load_3026 | 2 | T_bus3026_L | AB | 120 | wye-PQ
Load_3027 | 2 | T_bus3027_L | AB | 120 | wye-PQ
Load_3028 | 2 | T_bus3028_L | AB | 120 | wye-PQ
Load_3029 | 2 | T_bus3029_L | AB | 120 | wye-PQ
Load_3031 | 3 | T_bus3031_L | ABC | 208 | wye-PQ
Load_3032 | 3 | T_bus3032_L | ABC | 208 | wye-PQ
Load_3033 | 3 | T_bus3033_L | ABC | 208 | wye-PQ
Load_3034 | 3 | T_bus3034_L | ABC | 208 | wye-PQ
Load_3035 | 3 | T_bus3035_L | ABC | 208 | wye-PQ
Load_3036 | 3 | T_bus3036_L | ABC | 208 | wye-PQ
Load_3037 | 3 | T_bus3037_L | ABC | 208 | wye-PQ
Load_3038 | 3 | T_bus3038_L | ABC | 208 | wye-PQ
Load_3039 | 3 | T_bus3039_L | ABC | 208 | wye-PQ
Load_3041 | 2 | T_bus3041_L | AB | 120 | wye-PQ
Load_3042 | 2 | T_bus3042_L | AB | 120 | wye-PQ
Load_3043 | 2 | T_bus3043_L | AB | 120 | wye-PQ
Load_3044 | 2 | T_bus3044_L | AB | 120 | wye-PQ
Load_3045 | 2 | T_bus3045_L | AB | 120 | wye-PQ
Load_3047 | 3 | T_bus3047_L | ABC | 208 | wye-PQ
Load_3048 | 3 | T_bus3048_L | ABC | 208 | wye-PQ
Load_3049 | 3 | T_bus3049_L | ABC | 208 | wye-PQ
Load_3050 | 3 | T_bus3050_L | ABC | 208 | wye-PQ
Load_3051 | 3 | T_bus3051_L | ABC | 208 | wye-PQ
Load_3052 | 3 | T_bus3052_L | ABC | 208 | wye-PQ
Load_3054 | 3 | T_bus3054_L | ABC | 208 | wye-PQ
Load_3056 | 2 | T_bus3056_L | AB | 120 | wye-PQ
Load_3057 | 2 | T_bus3057_L | AB | 120 | wye-PQ
Load_3058 | 2 | T_bus3058_L | AB | 120 | wye-PQ
Load_3059 | 2 | T_bus3059_L | AB | 120 | wye-PQ
Load_3060 | 2 | T_bus3060_L | AB | 120 | wye-PQ
Load_3061 | 2 | T_bus3061_L | AB | 120 | wye-PQ
Load_3062 | 2 | T_bus3062_L | AB | 120 | wye-PQ
Load_3063 | 2 | T_bus3063_L | AB | 120 | wye-PQ
Load_3064 | 2 | T_bus3064_L | AB | 120 | wye-PQ
Load_3065 | 2 | T_bus3065_L | AB | 120 | wye-PQ
Load_3066 | 2 | T_bus3066_L | AB | 120 | wye-PQ
Load_3067 | 2 | T_bus3067_L | AB | 120 | wye-PQ
Load_3070 | 3 | T_bus3070_L | ABC | 208 | wye-PQ
Load_3071 | 3 | T_bus3071_L | ABC | 208 | wye-PQ
Load_3072 | 3 | T_bus3072_L | ABC | 208 | wye-PQ
Load_3073 | 3 | T_bus3073_L | ABC | 208 | wye-PQ
Load_3074 | 3 | T_bus3074_L | ABC | 208 | wye-PQ
Load_3077 | 3 | T_bus3077_L | ABC | 208 | wye-PQ
Load_3078 | 3 | T_bus3078_L | ABC | 208 | wye-PQ
Load_3081 | 3 | T_bus3081_L | ABC | 208 | wye-PQ
Load_3083 | 2 | T_bus3083_L | AB | 120 | wye-PQ
Load_3084 | 2 | T_bus3084_L | AB | 120 | wye-PQ
Load_3085 | 2 | T_bus3085_L | AB | 120 | wye-PQ
Load_3086 | 2 | T_bus3086_L | AB | 120 | wye-PQ
Load_3087 | 2 | T_bus3087_L | AB | 120 | wye-PQ
Load_3088 | 2 | T_bus3088_L | AB | 120 | wye-PQ
Load_3089 | 2 | T_bus3089_L | AB | 120 | wye-PQ
Load_3090 | 2 | T_bus3090_L | AB | 120 | wye-PQ
Load_3091 | 2 | T_bus3091_L | AB | 120 | wye-PQ
Load_3093 | 2 | T_bus3093_L | AB | 120 | wye-PQ
Load_3094 | 2 | T_bus3094_L | AB | 120 | wye-PQ
Load_3095 | 2 | T_bus3095_L | AB | 120 | wye-PQ
Load_3096 | 2 | T_bus3096_L | AB | 120 | wye-PQ
Load_3097 | 2 | T_bus3097_L | AB | 120 | wye-PQ
Load_3098 | 2 | T_bus3098_L | AB | 120 | wye-PQ
Load_3099 | 2 | T_bus3099_L | AB | 120 | wye-PQ
Load_3101 | 2 | T_bus3101_L | AB | 120 | wye-PQ
Load_3102 | 2 | T_bus3102_L | AB | 120 | wye-PQ
Load_3103 | 2 | T_bus3103_L | AB | 120 | wye-PQ
Load_3104 | 2 | T_bus3104_L | AB | 120 | wye-PQ
Load_3105 | 2 | T_bus3105_L | AB | 120 | wye-PQ
Load_3106 | 2 | T_bus3106_L | AB | 120 | wye-PQ
Load_3108 | 2 | T_bus3108_L | AB | 120 | wye-PQ
Load_3109 | 2 | T_bus3109_L | AB | 120 | wye-PQ
Load_3110 | 2 | T_bus3110_L | AB | 120 | wye-PQ
Load_3111 | 2 | T_bus3111_L | AB | 120 | wye-PQ
Load_3112 | 2 | T_bus3112_L | AB | 120 | wye-PQ
Load_3114 | 2 | T_bus3114_L | AB | 120 | wye-PQ
Load_3115 | 2 | T_bus3115_L | AB | 120 | wye-PQ
Load_3116 | 2 | T_bus3116_L | AB | 120 | wye-PQ
Load_3117 | 2 | T_bus3117_L | AB | 120 | wye-PQ
Load_3120 | 2 | T_bus3120_L | AB | 120 | wye-PQ
Load_3121 | 2 | T_bus3121_L | AB | 120 | wye-PQ
Load_3122 | 2 | T_bus3122_L | AB | 120 | wye-PQ
Load_3123 | 2 | T_bus3123_L | AB | 120 | wye-PQ
Load_3124 | 2 | T_bus3124_L | AB | 120 | wye-PQ
Load_3125 | 2 | T_bus3125_L | AB | 120 | wye-PQ
Load_3126 | 2 | T_bus3126_L | AB | 120 | wye-PQ
Load_3127 | 2 | T_bus3127_L | AB | 120 | wye-PQ
Load_3128 | 2 | T_bus3128_L | AB | 120 | wye-PQ
Load_3129 | 2 | T_bus3129_L | AB | 120 | wye-PQ
Load_3130 | 2 | T_bus3130_L | AB | 120 | wye-PQ
Load_3131 | 2 | T_bus3131_L | AB | 120 | wye-PQ
Load_3132 | 2 | T_bus3132_L | AB | 120 | wye-PQ
Load_3134 | 2 | T_bus3134_L | AB | 120 | wye-PQ
Load_3135 | 2 | T_bus3135_L | AB | 120 | wye-PQ
Load_3136 | 2 | T_bus3136_L | AB | 120 | wye-PQ
Load_3137 | 2 | T_bus3137_L | AB | 120 | wye-PQ
Load_3138 | 2 | T_bus3138_L | AB | 120 | wye-PQ
Load_3139 | 2 | T_bus3139_L | AB | 120 | wye-PQ
Load_3141 | 2 | T_bus3141_L | AB | 120 | wye-PQ
Load_3142 | 2 | T_bus3142_L | AB | 120 | wye-PQ
Load_3143 | 2 | T_bus3143_L | AB | 120 | wye-PQ
Load_3144 | 2 | T_bus3144_L | AB | 120 | wye-PQ
Load_3145 | 2 | T_bus3145_L | AB | 120 | wye-PQ
Load_3146 | 2 | T_bus3146_L | AB | 120 | wye-PQ
Load_3147 | 2 | T_bus3147_L | AB | 120 | wye-PQ
Load_3148 | 2 | T_bus3148_L | AB | 120 | wye-PQ
Load_3149 | 2 | T_bus3149_L | AB | 120 | wye-PQ
Load_3150 | 2 | T_bus3150_L | AB | 120 | wye-PQ
Load_3151 | 2 | T_bus3151_L | AB | 120 | wye-PQ
Load_3152 | 2 | T_bus3152_L | AB | 120 | wye-PQ
Load_3153 | 2 | T_bus3153_L | AB | 120 | wye-PQ
Load_3154 | 2 | T_bus3154_L | AB | 120 | wye-PQ
Load_3155 | 2 | T_bus3155_L | AB | 120 | wye-PQ
Load_3157 | 2 | T_bus3157_L | AB | 120 | wye-PQ
Load_3158 | 2 | T_bus3158_L | AB | 120 | wye-PQ
Load_3159 | 2 | T_bus3159_L | AB | 120 | wye-PQ
Load_3160 | 2 | T_bus3160_L | AB | 120 | wye-PQ
Load_3161 | 2 | T_bus3161_L | AB | 120 | wye-PQ
Load_3162 | 2 | T_bus3162_L | AB | 120 | wye-PQ

## Bus Coordinates
Bus Name | X | Y
bus1 | 10.52 | 13.6
bus1001 | 10.19 | 13.04
bus1002 | 8.9 | 14.11
bus1003 | 8.9 | 13.36
bus1004 | 7.77 | 14.11
bus1005 | 6.4 | 14.11
bus1006 | 5.15 | 14.11
bus1007 | 5.15 | 12.98
bus1008 | 3.71 | 14.11
bus1009 | 2.4 | 14.11
bus1010 | 1.4 | 14.11
bus1011 | 2.4 | 12.98
bus1012 | 2.4 | 12.11
bus1013 | 2.4 | 11.23
bus1014 | 3.85 | 11.23
bus1015 | 4.85 | 11.23
bus1016 | 2.4 | 10.48
bus1017 | 2.4 | 9.73
bus2001 | 10.52 | 12.23
bus2002 | 9.56 | 7.58
bus2003 | 8.3 | 7.58
bus2004 | 7.07 | 7.58
bus2005 | 5.77 | 7.58
bus2006 | 4.54 | 7.58
bus2007 | 4.55 | 8.25
bus2008 | 3.66 | 8.25
bus2009 | 4.55 | 8.93
bus2010 | 3.68 | 7.58
bus2011 | 2.71 | 7.58
bus2012 | 2.32 | 7.1
bus2013 | 2.31 | 6.44
bus2014 | 2.31 | 5.68
bus2015 | 1.41 | 5.68
bus2016 | 2.31 | 4.97
bus2017 | 2.31 | 4.24
bus2018 | 2.31 | 3.51
bus2019 | 3.23 | 6.45
bus2020 | 3.23 | 5.85
bus2021 | 4.04 | 6.44
bus2022 | 4.04 | 5.72
bus2023 | 4.04 | 4.99
bus2024 | 4.04 | 4.26
bus2025 | 4.04 | 3.53
bus2026 | 4.8 | 6.45
bus2027 | 5.59 | 6.45
bus2028 | 5.59 | 5.88
bus2029 | 5.58 | 5.31
bus2030 | 5.58 | 4.73
bus2031 | 5.58 | 4.16
bus2032 | 6.61 | 6.45
bus2033 | 7.6 | 6.45
bus2034 | 7.6 | 5.79
bus2035 | 8.46 | 6.44
bus2036 | 9.3 | 6.45
bus2037 | 10.21 | 6.45
bus2038 | 10.21 | 5.84
bus2039 | 10.21 | 4.98
bus2040 | 11.07 | 4.98
bus2041 | 11.88 | 4.98
bus2042 | 10.21 | 4.39
bus2043 | 10.21 | 3.63
bus2044 | 8.76 | 3.63
bus2045 | 8.76 | 4.29
bus2046 | 8.76 | 5
bus2047 | 7.84 | 4.29
bus2048 | 6.92 | 4.29
bus2049 | 7.87 | 3.63
bus2050 | 7.01 | 3.63
bus2051 | 6.16 | 3.62
bus2052 | 6.16 | 2.81
bus2053 | 8.76 | 2.1
bus2054 | 7.78 | 2.1
bus2055 | 6.84 | 2.1
bus2056 | 5.86 | 2.1
bus2057 | 8.76 | 1.4
bus2058 | 9.9 | 1.4
bus2059 | 7.72 | 1.4
bus2060 | 6.76 | 1.4
bus3001 | 10.83 | 13.02
bus3002 | 12.5 | 12.16
bus3003 | 12.5 | 12.85
bus3004 | 12.5 | 13.43
bus3005 | 13.36 | 12.85
bus3006 | 13.36 | 13.91
bus3007 | 13.36 | 14.71
bus3008 | 14.62 | 11.41
bus3009 | 14.61 | 12.04
bus3010 | 14.62 | 12.7
bus3011 | 14.61 | 13.36
bus3012 | 14.62 | 14.02
bus3013 | 14.61 | 10.77
bus3014 | 14.62 | 10.06
bus3015 | 15.79 | 11.41
bus3016 | 15.8 | 10.75
bus3017 | 15.8 | 10.1
bus3018 | 15.8 | 12.07
bus3019 | 15.8 | 12.72
bus3020 | 15.8 | 13.38
bus3021 | 15.8 | 14.03
bus3022 | 16.99 | 11.41
bus3023 | 16.99 | 10.76
bus3024 | 16.99 | 10.12
bus3025 | 16.99 | 9.47
bus3026 | 16.99 | 12.06
bus3027 | 16.99 | 12.72
bus3028 | 16.99 | 13.38
bus3029 | 16.99 | 14.03
bus3030 | 18.26 | 11.41
bus3031 | 18.26 | 10.91
bus3032 | 18.26 | 10.4
bus3033 | 18.26 | 9.9
bus3034 | 18.26 | 9.39
bus3035 | 18.25 | 12.05
bus3036 | 18.27 | 12.68
bus3037 | 18.25 | 13.32
bus3038 | 18.25 | 13.95
bus3039 | 18.26 | 14.59
bus3040 | 19.51 | 11.41
bus3041 | 19.51 | 10.87
bus3042 | 19.51 | 10.33
bus3043 | 19.51 | 9.79
bus3044 | 19.51 | 12.03
bus3045 | 19.51 | 12.63
bus3046 | 20.88 | 11.41
bus3047 | 20.88 | 12.16
bus3048 | 21.17 | 10.92
bus3049 | 22 | 10.92
bus3050 | 22.82 | 10.92
bus3051 | 23.64 | 10.92
bus3052 | 24.46 | 10.91
bus3053 | 19.51 | 14.79
bus3054 | 19.51 | 14.19
bus3055 | 21.01 | 14.79
bus3056 | 21.5 | 15.2
bus3057 | 22.22 | 15.2
bus3058 | 22.93 | 15.2
bus3059 | 23.65 | 15.2
bus3060 | 24.37 | 15.2
bus3061 | 25.09 | 15.2
bus3062 | 21.53 | 14.13
bus3063 | 22.24 | 14.13
bus3064 | 22.95 | 14.14
bus3065 | 23.66 | 14.13
bus3066 | 24.38 | 14.13
bus3067 | 25.09 | 14.13
bus3068 | 18.26 | 8.82
bus3069 | 16.65 | 8.82
bus3070 | 16.65 | 8.27
bus3071 | 16.65 | 7.71
bus3072 | 16.65 | 7.16
bus3073 | 15.76 | 8.82
bus3074 | 14.98 | 8.82
bus3075 | 19.05 | 8.82
bus3076 | 19.97 | 8.82
bus3077 | 20.73 | 8.82
bus3078 | 21.49 | 8.82
bus3079 | 19.97 | 8.07
bus3080 | 19.97 | 7.42
bus3081 | 19.21 | 7.42
bus3082 | 19.97 | 6.79
bus3083 | 19.1 | 6.79
bus3084 | 18.23 | 6.79
bus3085 | 17.36 | 6.79
bus3086 | 16.49 | 6.79
bus3087 | 15.62 | 6.79
bus3088 | 14.75 | 6.79
bus3089 | 13.88 | 6.79
bus3090 | 13.01 | 6.79
bus3091 | 12.14 | 6.79
bus3092 | 22.05 | 6.79
bus3093 | 22.07 | 7.3
bus3094 | 22.04 | 7.81
bus3095 | 22.05 | 8.32
bus3096 | 22.05 | 8.83
bus3097 | 22.05 | 9.34
bus3098 | 22.05 | 6.13
bus3099 | 22.05 | 5.56
bus3100 | 23.09 | 6.8
bus3101 | 23.86 | 6.8
bus3102 | 24.53 | 6.8
bus3103 | 25.12 | 6.8
bus3104 | 23.09 | 7.52
bus3105 | 23.08 | 8.08
bus3106 | 23.09 | 8.67
bus3107 | 19.98 | 5.54
bus3108 | 18.97 | 5.54
bus3109 | 18.07 | 5.54
bus3110 | 16.97 | 5.54
bus3111 | 15.97 | 5.54
bus3112 | 15.07 | 5.54
bus3113 | 18.63 | 4.76
bus3114 | 18.63 | 4.15
bus3115 | 18.63 | 3.53
bus3116 | 17.55 | 4.75
bus3117 | 16.55 | 4.76
bus3118 | 21.36 | 4.03
bus3119 | 22.77 | 4.03
bus3120 | 22.77 | 4.69
bus3121 | 22.78 | 5.34
bus3122 | 22.78 | 5.96
bus3123 | 23.64 | 4.04
bus3124 | 24.42 | 4.04
bus3125 | 25.17 | 4.04
bus3126 | 25.97 | 4.04
bus3127 | 25.97 | 4.58
bus3128 | 25.97 | 5.12
bus3129 | 25.97 | 5.66
bus3130 | 25.97 | 6.2
bus3131 | 25.97 | 6.75
bus3132 | 21.35 | 3.22
bus3133 | 21.36 | 2.41
bus3134 | 22.53 | 2.41
bus3135 | 23.57 | 2.41
bus3136 | 24.53 | 2.41
bus3137 | 21.37 | 1.79
bus3138 | 21.37 | 1.16
bus3139 | 21.36 | 0.53
bus3140 | 17.61 | 2.5
bus3141 | 18.42 | 2.48
bus3142 | 19.23 | 2.48
bus3143 | 20.03 | 2.49
bus3144 | 18.31 | 1.11
bus3145 | 18.99 | 1.11
bus3146 | 19.67 | 1.11
bus3147 | 20.35 | 1.11
bus3148 | 16.87 | 2.48
bus3149 | 16.13 | 2.48
bus3150 | 15.4 | 2.48
bus3151 | 14.66 | 2.48
bus3152 | 13.92 | 2.48
bus3153 | 13.18 | 2.48
bus3154 | 12.44 | 2.49
bus3155 | 11.7 | 2.49
bus3156 | 17.64 | 1.11
bus3157 | 16.9 | 1.11
bus3158 | 16.17 | 1.11
bus3159 | 15.43 | 1.11
bus3160 | 14.7 | 1.11
bus3161 | 13.97 | 1.11
bus3162 | 13.23 | 1.11